## DEC-G4  Diesel Fire Pump Controllers				      MASTER

---------- EQUIPMENT ORDERED ----------

COMPLETE CONTROLLER MODEL NO.

IN TYPE 12 DUST TIGHT ENCLOSURE (OR AS INDICATED BELOW)

FOR USE WITH       VDC       GROUND SYSTEM FOR TWO BATTERY UNITS

EACH HAVING (QTY)       TYPE       CELLS WITH MAX. CAPACITY SHOWN BELOW

INPUT POWER       VAC AT       HZ.  SINGLE PHASE       AMP MAX.

(BRANCH CIRCUIT REQUIRED.  15 AMP BRANCH IS ADEQUATE).

ENGINE MAKE           ENGINE MODEL

##### MODEL

DEC – 12 VDC, NEG GROUND, 115 VAC			 DEC – 24 VDC, NEG GROUND, 115 VAC

DEC – 12 VDC, NEG GROUND, 230 VAC			 DEC – 24 VDC, NEG GROUND, 230 VAC

DEC – 12 VDC, POS  GROUND, 115  VAC			 DEC – 24 VDC, POS  GROUND, 115 VAC

DEC – 12 VDC, POS  GROUND, 230 VAC			 DEC – 24 VDC, POS  GROUND, 230 VAC

INCLUDES 8 ADDITIONAL PUMP HOUSE TROUBLE INPUTS (USER DEFINEABLE)

##### AND 8 REMOTE ALARM CONTACTS AS DESCRIBED BELOW

Contacts are rated 6 amps at 30 VDC, 6 amps at 250 VAC.  UL pilot duty ratings R300 and B300.  Relays can be programmed for any of the following: Auto Off, Battery Failure, Charge Failure, Electronic Engine Alarms (301-304, 310-312), Failure to Start, High Water, Lockout, Low Discharge Pressure, Low Fuel, Low Oil, Low Suction Pressure, Low Zone (On Demand), Over Pressure, Overspeed, Pump House Trouble, Pump Run, Start Contactor Failure, Transducer Failure.

INCLUDES MODIFICATIONS CHECKED BELOW:

(CONTROLLER MODEL NUMBER INDICATES MODIFICATIONS SUPPLIED)

FC     – FOAM CONTROLLER				 16A   – 500 PSI, PRESSURE TRANSDUCER, TEST VALVE

3R     – TYPE 3R RAINTIGHT ENCLOSURE		                   SOLENOID & WET PARTS

4        – TYPE 4 WATERTIGHT ENCLOSURE		 19      –  SPACE HEATER

4XB  – TYPE 4X, 304 SS WATERTIGHT ENCLOSURE	 20      –  SPACE HEATER WITH THERMOSTAT

4XC  – TYPE 4X, 316 SS WATERTIGHT ENCLOSURE	 20A   –  SPACE HEATER WITH HUMIDISTAT

8E     – CE DECLARATION FOR EUROPEAN COMM.	 32      –  LOW PUMP ROOM TEMPERATURE SWITCH

12B   – ADDS 36” BASE CABINET FOR 72” HEIGHT	 48E    –  EMAIL NOTIFICATIONS THROUGH ETHERNET

12L   – ADDS 18” PAINTED LEGS TO CONTROLLER 	 48F    –  LOCAL MODBUS RTU CONNECTION

15     –  300 PSI, 316 SS PRESSURE TRANSDUCER,		 83LT –  LOW SUCTION TRANSDUCER & WET PARTS

TEST VALVE SOLENOID & WET PARTS

15A  –  300 PSI, 300 SERIES SS TRANSDUCER,

TEST VALVE SOLENOID & WET PARTS

ORDER ALSO INCLUDES:

4817 – LOW FUEL SWITCH (SHIPPED LOOSE FOR FIELD INSTALLATION)

4817L – LONG ROD LOW FUEL LEVEL SWITCH (FOR LARGER DIAMETER OR TALL TANKS)

6288 – HIGH FUEL SWITCH (SHIPPED LOOSE FOR FIELD INSTALLATION)

REMOTE ALARM PANEL        FOR REMOTE INSTALLATION AT A POINT OF CONSTANT ATTENDANCE

JOB IDENTIFICATION:

| Master Control Systems, Inc. LAKE BLUFF, ILLINOIS U.S.A | DEC ORDER SELECTION DRAWING | Date: 24 July 2019 |
| --- | --- | --- |
|  |  | Drawing 22899 Issue 2 |